Part III Form 2

Section 11.  ANNUAL REPORT.

| Drinking-Water System Number: | 220013562 |
| --- | --- |
| Drinking-Water System Name: | South River WTP |
| Drinking-Water System Owner: | The Corporation of the Municipality of South River |
| Drinking-Water System Category: | Large Municipal Residential |
| Period being reported: | Jan 1, 2015 to Dec 31, 2015 |

| Complete if your Category is Large Municipal Residential or Small Municipal Residential South River Municipal Office, 93 Ottawa Street, South River, Ontario Does your Drinking-Water System serve more than 10,000 people? Yes [ ] No [X] Is your annual report available to the public at no charge on a web site on the Internet? Yes [ ] No [X] Location where Summary Report required under O. Reg. 170/03 Schedule 22 will be available for inspection. | Complete for all other Categories. Number of Designated Facilities served: Did you provide a copy of your annual report to all Designated Facilities you serve? Yes [ ] No [ ] Number of Interested Authorities you report to: Did you provide a copy of your annual report to all Interested Authorities you report to for each Designated Facility? Yes [ ] No [ ] |
| --- | --- |

Note: For the following tables below, additional rows or columns may be added or an appendix may be attached to the report

List all Drinking-Water Systems, which receive all of their drinking water from your system:

| Drinking Water System Name | Drinking Water System Number |
| --- | --- |
| NA |  |

Did you provide a copy of your annual report to all Drinking-Water System owners that are connected to you and to whom you provide all of its drinking water?

Yes [  ] No [  ]

Indicate how you notified system users that your annual report is available, and is free of charge.

[X] Public notice via the web  	Notice to be posted on the Village website.

[X] Public access/notice via Government Office   Water System Information binder is available for public review at the municipal office.

[  ] Public access/notice via a newspaper

[  ] Public access/notice via Public Request

[  ] Public access/notice via a Public Library

[X] Public notice via other method:   	A newsletter is included Bi-monthly with the municipal utility billing.

Description of the South River Drinking-Water System

The South River Water Treatment facility, owned by the Village of South River, was commissioned in May of 2000. The plant provides full conventional treatment to raw water drawn from Forest Lake, a dam controlled section of the South River. Treatment consists of chemically assisted coagulation, flocculation, clarification and filtration in duel package plants followed by disinfection with Sodium Hypochlorite before entering the distribution system. This is a pressurized system due to there being no elevated treated water storage reservoir in the community.

The plant raw water intake consists of a 300 mm diameter intake pipe extending 232 m into Forest Lake, with a flared elbow in a wooden and concrete crib located at a depth of 4.5 m.

The low lift pumping station is located approx. 170 m south of Howard Street off the gravel access road. The low lift pumping station consists of a raw water well, dual manual screens and three (3) submersible pumps (two duty pumps and one standby), each rated at 10.0 L/s at 11.0 m of TDH that pump water to the treatment plant.

The water treatment facility consists of Two (2) Conventional Napier Reid package plants each rated at 840 m3/d with flocculation tanks, up flow clarifiers, and filters each consisting of triple media that includes Garnet Sand, Silica Sand and Granular Activated Carbon both with surface areas of 4.49 m2.

The chemical feed system consists of two (2) coagulant metering pumps, one (1) duty and one (1) standby, each with the capacity of 5 L/hour and one (1) 15 m3 storage tank; Two (2) (polymer) metering pumps, each with a capacity of 8 L/hour and one (1) 1350 L storage tank; three (3) alkalinity and pH adjustment (sodium hydroxide) metering pumps with a capacity of 3 L/hour and one (1) 1350 L storage tanks; four (4) primary and post disinfection (sodium hypochlorite) metering pumps, three (3) duty, and one standby, each rated at 3 L/hour and a 450 L storage tank.

An in ground clearwell reservoir located under the facility has the approximate capacity of 1,536 m3 of useable storage.

Raw water entering the plant is injected with sodium hydroxide and aluminum sulphate. Following rapid mixing, the water flows into the flocculation tank. A polymer can be injected into the floculator chamber as a coagulant aid. Treated water overflows from the clarifiers through two multi media filters consisting of garnet/sand/ anthracite. Filtered water is then injected with a 12% sodium hypochlorite solution and directed to a baffled clear well reservoir located beneath the plant. Treated water is pumped from the clearwell, and directed to the distribution system by a high lift pumping system. A second chlorination point and pH adjustment is available prior to the point of entry to the distribution system, if needed.

The water supply system is a pressurized system. High lift pumps at the treatment facility run continually to maintain water pressure in the water distribution system piping which delivers the treated water to the systems users. There are four high lift pumps, two (2) pumps each rated at 7 L/s at a TDH of 45m; two (2) pumps each rated at 14 L/s at a TDH of 45m.  The high lift pumps are controlled by variable frequency drives and sequence automatically to maintain system pressure and flow demands. In addition there are two (2) high lift fire pumps each rated at 56 L/s at a TDH of 38m.

Standby emergency power is provided by one (1) 135 kW radiator cooled diesel generator housed in a separate building.  It has one (1) double walled external fuel tank with the capacity of 1135 liters for diesel fuel storage.

The treatment facility has a full SCADA instrumentation system to monitor and control plant operations.

The South River distribution system consists of a mixture of cast iron, ductile iron, asbestos and PVC piping ranging in size from 300mm in diameter down to 50mm diameter.  As of December 2010 there is:  250m of 50mm, 1984m of 100mm, 6657m of 150mm, 1401m of 200mm, 1451m of 250mm, and 685m of 300mm. The length of the entire system is therefore approximately 12.43 km. There are 11 dead end locations and 66 fire hydrants. There is no water storage tower or reservoir in the distribution system.

List all water treatment chemicals used over this reporting period

Sodium Hypochlorite Aluminum Sulfate Sodium Hydroxide Magnafloc LT25 Poly Acrylamide Polymer

Were any significant expenses incurred to?

[  ] Install required equipment

[X]  Repair required equipment

[ X]  Replace required equipment

# Describe

DWQMS $875 Dosing pump diaphragms, membrane caps and supplies $3,076 Filter bags for sludge bagger $838 Supernatant pump $3,497 pH sensors for analyzers $2,570 Vacuum truck for filter media replacement $1,045 Low lift pump repair $2,060 Replacement media for filter train 2 $15,827 3 phase 600 VLT space heating unit at the low lift station $892

Provide details on the notices submitted in accordance with subsection 18(1) of the Safe Drinking-Water Act or section 16-4 of Schedule 16 of O.Reg.170/03 and reported to Spills Action Centre

| Incident Date | Parameter | Result | Unit of Measure | Corrective Action | Corrective Action Date | AWQI# |
| --- | --- | --- | --- | --- | --- | --- |
| N/A |  |  |  |  |  |  |

Microbiological testing done under section 8-2during this reporting period.

|  | Number of Samples EC & TC | Range of E.Coli Or Fecal Results (min #)-(max # | Range of Total Coliform Results (min #)-(max #) | Number of HPC Samples | Range of HPC Results (min #)-(max #) |
| --- | --- | --- | --- | --- | --- |
| Raw | 52 | 0-40 | 24 - 2160 | NA | NA |
| Treated | 53 | 0 – 0 | 0 - 0 | 53 | 0 – 1 |
| Distribution | 157 | 0 - 0 | 0 - 0 | 53 | 0 - 1 |

Operational testing done under Schedule 7, 8 or 9 of Regulation 170/03 during the period covered by this Annual Report.

Filter SCADA Summary

|  | Number of Samples | Range of Results |
| --- | --- | --- |
| Filter 1 Turbidity | 8760 | 0.0 to 1.82 NTU |
| Filter 1 turb grab | 40 | 0.025 to 0.13 NTU |
| Filter 2 Turbidity | 8760 | 0.0 to 2.6 NTU |
| Filter 2 Turb grab | 38 | 0.01 to 0.121 NTU |

POE Grabs

|  | Number of Samples | Range of Results |
| --- | --- | --- |
| Free Chlorine | 78 | 1.81 – 3.32 mg/L |

Distribution Grabs

|  | Number of Samples | Range of Results |
| --- | --- | --- |
| Free Chlorine | 368 | 0.06 – 2.8 mg/L |

POE Online Continuous Analyzers

| Parameter | # samples | Range of Results |
| --- | --- | --- |
| Online POE Free Chlorine | 8760 | 0 – 5.0 mg/L |

NOTE: For continuous monitors use 8760 as the number of samples.

Summary of additional testing and sampling carried out in accordance with the requirement of an approval or order.

(* The average annual concentration of suspended solids in the effluent discharged from the backwash wastewater facilities shall not exceed 25 mg/L)

| Date of legal instrument issued | Parameter | Date Sampled | Result | Unit of Measure |
| --- | --- | --- | --- | --- |
|  |  | Jan 15 | 30 | mg/L |
|  |  | Feb 15 | 13 | mg/L |
| MDWL 200-101, May 27, 2011 | Backwash TSS | Mar 15 | 34 | mg/L |
|  |  | Apr 15 | 26 | mg/L |
|  |  | May 15 | 24 | mg/L |
|  |  | June 15 | 20 | mg/L |
|  |  | Jul 15 | 8 | mg/L |
|  |  | Aug 15 | 13 | mg/L |
|  |  | Sep 15 | 33 | mg/L |
|  |  | Oct 15 | 7 | mg/L |
|  |  | Nov 15 | 18 | mg/L |
|  |  | Dec 15 | 18 | mg/L |
|  |  | Average | 20.33 | mg/L |

Summary of Inorganic parameters tested during this reporting period or the most recent

| # Parameter | # Sample Date | Result Value | # Unit of Measure | # Exceedance |
| --- | --- | --- | --- | --- |
| ## Antimony | 20 Jan 2015 | <0.02 | ug/L | No |
| Arsenic | 20 Jan 2015 | <0.2 | ug/L | No |
| Barium | 20 Jan 2015 | 13.3 | ug/L | No |
| Boron | 20 Jan 2015 | 4.9 | ug/L | No |
| Cadmium | 20 Jan 2015 | 0. 008 | ug/L | No |
| ## Chromium | 20 Jan 2015 | 0.06 | ug/L | No |
| Mercury | 20 Jan 2015 | 0.03 | mg/L | No |
| Selenium | 20 Jan 2015 | <1 | ug/L | No |
| Sodium | 20 Jan 2015 | 22.2 | mg/L | Yes |
| Uranium | 20 Jan 2015 | <0.002 | ug/L | No |
| Fluoride | 08 Mar 2011 | <0.1 | mg/L | No |
| Nitrite | 20 Jan 2015 06 May 2015 30 July 2015 03 Nov 2015 | <0.003 <0.003 <0.003 <0.003 | mg/L mg/L mg/L mg/L | No No No No |
| Nitrate | 20 Jan 2015 06 May 2015 30 July 2015 03 Nov 2015 | 0.128 0.149 0.063 0.070 | mg/L mg/L mg/L mg/L | No No No No |

Summary of samples reported to comply with O. Reg. 170/03 Schedule 15.1: Lead

| Round 1 Dec 15 2014 to Apr 15 2015 | Number of Lead Samples | Number of Adverse Results | Number of Hydrants Sampled | Range of Lead Samples (ug/L) |  |  | Range of PH Sample Results |  | Range of Alkalinity Sample Results (mg/L as CaCO3) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | MIN | MAX | MIN | MAX | MIN | MAX |
| Distribution | 2 | 0 | 2 |  | <0.001 | <0.001 | 6.33 | 6.33 | 5.99 | 6.42 |
| Non-Residential | 0 | 0 | N/A |  | N/A | N/A | N/A | N/A | NA | NA |
| Residential | 0 | 0 | N/A |  | N/A | N/A | N/A | N/A | NA | NA |
| Round 2 June 15 2015 to Oct 15 2015 | Number of Lead Samples | Number of Adverse Results | Number of Hydrants Sampled |  | Range of Lead Samples (ug/L) |  | Range of PH Sample Results |  | Range of Alkalinity Sample Results (mg/L as CaCO3) |  |
|  |  |  |  |  | MIN | MAX | MIN | MAX | MIN | MAX |
| Distribution | 0 | 0 | 2 |  | <0.001 | <0.001 | 6.14 | 6.14 | 5.56 | 6.42 |
| Non-Residential | 0 | 0 | N/A |  | N/A | N/A | N/A | N/A | NA | NA |
| Residential | 0 | 0 | N/A |  | N/A | N/A | N/A | N/A | NA | NA |

Summary of Organic parameters sampled during this reporting period or the most recent

| Parameter | # Sample Date | Result Value | # Unit of Measure | # Exceedance |
| --- | --- | --- | --- | --- |
| Alachlor | 20 Jan 2015 | <0.02 | ug/L | No |
| Aldicarb | 20 Jan 2015 | <0.01 | ug/L | No |
| Aldrin | 20 Jan 2015 | <0.01 | ug/L | No |
| Aldrin + Dieldrin | 20 Jan 2015 | <0.01 | ug/L | no |
| Atrazine | 20 Jan 2015 | <0.01 | ug/L | No |
| Atrazine + Desethyl-atrazine | 20 Jan 2015 | <0.01 | ug/L | No |
| Atrazine + N-dealkylated metobolites | 20 Jan 2015 | <0.01 | ug/L | No |
| Azinphos-methyl Guthion | 20 Jan 2015 | <0.02 | ug/L | No |
| Bendiocarb | 20 Jan 2015 | <0.01 | ug/L | No |
| Benzene | 20 Jan 2015 | <0.32 | ug/L | No |
| Benzo(a)pyrene | 20 Jan 2015 | <0.004 | ug/L | No |
| Bromoxynil | 20 Jan 2015 | <0.33 | ug/L | No |
| Carbaryl | 20 Jan 2015 | <0.01 | ug/L | No |
| Carbofuran | 20 Jan 2015 | <0.01 | ug/L | No |
| Carbon Tetrachloride | 20 Jan 2015 | <0.16 | ug/L | No |
| g-Clorodane | 20 Jan 2015 | <0.01 | ug/L | No |
| a-Clorodane | 20 Jan 2015 | <0.01 | ug/L | No |
| Chlordane (Total) | 20 Jan 2015 | <0.01 | ug/L | No |
| Chlorpyrifos | 20 Jan 2015 | <0.02 | ug/L | No |
| Cyanazine | 20 Jan 2015 | <0.03 | ug/L | No |
| Desethyl-atrazine | 20 Jan 2015 | <0.01 | ug/L | No |
| Diazinon | 20 Jan 2015 | <0.02 | ug/L | No |
| Dicamba | 20 Jan 2015 | <0.20 | ug/L | No |
| Dieldrin | 20 Jan 2015 | <0.01 | ug/L | No |
| 1,2-Dichlorobenzene | 20 Jan 2015 | <0.41 | ug/L | No |
| 1,4-Dichlorobenzene | 20 Jan 2015 | <0.36 | ug/L | No |
| Dichlorodiphenyltrichloroethane (DDT) + metabolites | 20 Jan 2015 | <0.01 | ug/L | No |
| 1,2-Dichloroethane | 20 Jan 2015 | <0.35 | ug/L | No |
| 1,1-Dichloroethylene (vinylidene chloride) | 20 Jan 2015 | <0.33 | ug/L | No |
| Dichloromethane (Methylene Chloride) | 20 Jan 2015 | <0.35 | ug/L | No |
| 2-4 Dichlorophenol | 20 Jan 2015 | <0.15 | ug/L | No |
| 2,4-Dichlorophenoxy acetic acid (2,4-D) | 20 Jan 2015 | <0.19 | ug/L | no |
| Diclofop-methyl | 20 Jan 2015 | <0.40 | ug/L | No |
| Dimethoate | 20 Jan 2015 | <0.03 | ug/L | No |
| Dinoseb | 20 Jan 2015 | <0.36 | ug/L | No |
| Diquat | 20 Jan 2015 | <1 | ug/L | No |
| Diuron | 20 Jan 2015 | <0.03 | ug/L | No |
| Glyphosate | 20 Jan 2015 | <1 | ug/L | no |
| Heptachlor | 20 Jan 2015 | <0.01 | ug/L | No |
| Heptachlor Epoxide | 20 Jan 2015 | <0.01 | ug/L | No |
| Heptachlor + Heptachlor Epoxide | 20 Jan 2015 | <0.01 | ug/L | No |
| Lindane (Total) | 20 Jan 2015 | <0.01 | ug/L | No |
| Malathion | 20 Jan 2015 | <0.02 | ug/L | No |
| Methoxychlor | 20 Jan 2015 | <0.01 | ug/L | No |
| Metolachlor | 20 Jan 2015 | <0.01 | ug/L | No |
| Metribuzin | 20 Jan 2015 | <0.02 | ug/L | No |
| Monochlorobenzene | 20 Jan 2015 | <0.3 | ug/L | no |
| Oxychlordane | 20 Jan 2015 | <0.01 | ug/L | No |
| Paraquat | 20 Jan 2015 | <1 | ug/L | no |
| Parathion | 20 Jan 2015 | <0.02 | ug/L | No |
| Pentachlorophenol | 20 Jan 2015 | <0.15 | ug/L | No |
| Phorate | 20 Jan 2015 | <0.01 | ug/L | No |
| Picloram | 20 Jan 2015 | <1 | ug/L | No |
| Polychlorinated Biphenyls(PCB) | 20 Jan 2015 | <0.04 | ug/L | No |
| p.p-DDE | 20 Jan 2015 | <0.01 | ug/L | No |
| p.p-DDD | 20 Jan 2015 | <0.01 | ug/L | No |
| o.p-DDT | 20 Jan 2015 | <0.01 | ug/L | No |
| p.p-DDT | 20 Jan 2015 | <0.01 | ug/L | No |
| Prometryne | 20 Jan 2015 | <0.03 | ug/L | No |
| Simazine | 20 Jan 2015 | <0.01 | ug/L | No |
| Temephos | 20 Jan 2015 | <0.01 | ug/L | no |
| Terbufos | 20 Jan 2015 | <0.01 | ug/L | No |
| Tetrachloroethylene | 20 Jan 2015 | <0.35 | ug/L | No |
| 2,3,4,6-Tetrachlorophenol | 20 Jan 2015 | <0.20 | ug/L | no |
| Triallate | 20 Jan 2015 | <0.01 | ug/L | No |
| Trichloroethylene | 20 Jan 2015 | <0.44 | ug/L | No |
| 2,4,6-Trichlorophenol | 20 Jan 2015 | <0.25 | ug/L | No |
| 2,4,5-Trichlorophenoxy acetic acid (2,4,5-T) | 20 Jan 2015 | <0.22 | ug/L | No |
| Trifluralin | 20 Jan 2015 | <0.02 | ug/L | No |
| Vinyl Chloride | 20 Jan 2015 | <0.17 | ug/L | No |

| THM Dist Sample Location 22 Kilper St Result marked with * not used in calculating the annual average. The regulation requires that the highest result from each quarter be used to calculate the average | 1 st Quarter Result Value | 2 nd Quarter Result Value | 3 rd Quarter Result Value | 4th Quarter Result Value | Unit of Measure | Exceedance |
| --- | --- | --- | --- | --- | --- | --- |
| Date Sampled | 20 Jan 15 | 06 May 15 | 30 July 15 | 03 Nov 15 |  |  |
| Bromodichloromethane | 1.1 | 1.4 | 2.8 | 1.7 | ug/L | No |
| Bromoform | < 0.34 | < 0.34 | < 0.34 | < 0.34 | ug/L | No |
| Chloroform | 28 | 42 | 57 | 23 | ug/L | No |
| Dibromochloromethane | < 0.37 | < 0.37 | < 0.37 | < 0.37 | ug/L | No |
| Total Trihalomethanes | 29 | 43 | 60 | 25 | ug/L | No |
| Total Trihalomethanes 4 Quarter Average |  |  |  | 39.25 | ug/L | No |

List any Inorganic or Organic parameter(s) that exceeded half the standard prescribed in Schedule 2 of Ontario Drinking Water Quality Standards.

| #### Parameter | Result Value | Unit of Measure | #### ½ MAC VALUE | MAC Value | #### Date of Sample |
| --- | --- | --- | --- | --- | --- |
| #### THM | 60 | ug/L | 50 | 100 | 30 July 15 |